## Worksheet
Blind Flange DIN steel insert injection moulded+drilled PN10 Flange connection PP-FRP black
Code: 14.045
The torques nm[NM] specified in the technical catalogue are to be used as maximum values.
Dimension | Code | Detail | da(OD) mm | da inch | d mm | Tol+ | Tol- | d2 mm | Tol+ | Tol- | b mm | Tol+ | Tol- | k mm | Tol+ | Tol- | p bar | DN mm | K mm | nm [NM] | numb pc | Weight
200/225 | 14.045.0200.11 | 200/225 - MOP 16 bar | 200 | 8 | 340 | 3 | 3 | 22 | 0.75 | 0.75 | 25 | 0.75 | 0.75 | 295 | 0.75 | 0.75 | 16 | 200 | M20 | 120 | 8 | 6.495
250/280 | 14.045.0250.11 | 250/280 - MOP 16 bar | 250 | 10 | 409 | 4.5 | 4.5 | 22 | 0.75 | 0.75 | 30 | 0.75 | 0.75 | 350 | 0.75 | 0.75 | 16 | 250 | M20 | 130 | 12 | 15.4
315 | 14.045.0315.11 | 315 - MOP 16 bar | 315 | 12 | 463 | 4.5 | 4.5 | 22 | 0.75 | 0.75 | 34 | 0.75 | 0.75 | 400 | 0.75 | 0.75 | 16 | 300 | M20 | 130 | 12 | 25.8
355 | 14.045.0355.11 | 355 - MOP 16 bar | 355 | 13 | 515 | 4.5 | 4.5 | 22 | 0.75 | 0.75 | 42 | 0.75 | 0.75 | 460 | 0.75 | 0.75 | 16 | 350 | M20 | 160 | 16 | 39.4
400 | 14.045.0400.11 | 400 - MOP 16 bar | 400 | 14 | 574 | 4.5 | 4.5 | 27 | 0.75 | 0.75 | 46 | 0.75 | 0.75 | 515 | 0.75 | 0.75 | 16 | 400 | M24 | 170 | 16 | 50.44
04/07/2026 11:19